## Sheet1
Overall Data Center Costs
Assumptions
| Cost of power ($/kwh): | 0.07
| Cost of Facility ($): | 200000000
| Facilities Amortization: | 180 |  | (15 years)
| Number of Servers: | 50000
| Cost/Server ($) | 2000
| Server Amortization (months) | 36 |  | (3 years)
| Size of Facility (Critical Load MW): | 15000000 |  | (15MW)
| Annual Cost of Money (%): | 5%
| Average Power Usage (%): | 80% |  | (Average % of provisioned power used)
| Power Usage Effectiveness | 1.7
| Power and Cooling Infrastrucure (%) | 82% |  | (% of infrastructure that is power & cooling)
Network egress charges not included (workload dependent)
Calculations
| Infrastructure | 1581587.2535 | [=-PMT(CostOfMoney/12,FacilityAmortization,FacilityCost,0)]
| Servers | 2997089.7105 | [=-PMT(CostOfMoney/12, ServerAmortization, ServerCount*ServerCost, 0)]
| Power & Cooling Infrastructure | 1296901.5479 | [=InfrastructureMonthly*PowerAndCoolikngInfrastructurePercentage]
| Power | 1042440 | [=MegaWattsCriticalLoad*AveragePowerUsage/1000*PUE*PowerCost*24*365/12]
| Other Infrastructure | 284685.7056 | [=+InfrastructureMonthly-PowerAndCoolingInfrastructureMonthly]
| Full burdened Power | 2339341.5479 | [=+PowerAndCoolingInfrastructureMonthly+PowerMonthly]
| Total: | 5621116.9639